# Micro-CTL Automation Sdn. Bhd.

## MICTRON 9900

###### ANALOGUE ADDRESSABLE

###### FIRE ALARM SYSTEM

## ENGINEERING SPECIFICATION

| TABLE OF CONTENTS |  |  |  | Page |
| --- | --- | --- | --- | --- |
| 1.0 |  | Scope of works ............................................................................................................................................... |  | 3 |
| 2.0 |  | General requirements ..................................................................................................................................... |  | 4 |
| 3.0 |  | System requirements ...................................................................................................................................... |  | 5 |
| 4.0 |  | Functional requirements ................................................................................................................................. |  | 6 |
|  | 4.1 | Alarm condition ............................................................................................................................................. |  | 6 |
|  | 4.2 | Fault warning condition ................................................................................................................................. |  | 6 |
| 5.0 |  | System descriptions ....................................................................................................................................... |  | 7 |
|  | 5.1 | System configuration ..................................................................................................................................... |  | 7 |
|  | 5.2 | Main Fire Alarm Panel (MFAP) .................................................................................................................... |  | 7 |
|  |  | 5.2.1 | System Control Display (Central Controller) ................................................................................ | 7 |
|  |  | 5.2.2 | Fire Zone Display ............................................................................................................................ | 7 |
|  |  | 5.2.3 | Information Display ........................................................................................................................ | 7 |
|  |  | 5.2.4 | Mimic Panel ................................................................................................................................... | 8 |
|  |  | 5.2.5 | Battery Charger ............................................................................................................................... | 8 |
|  |  | 5.2.6 | 24 volts DC battery set ................................................................................................................... | 8 |
|  | 5.3 | Fire detection sensors, monitoring sensors, control outputs and alarm initiating devices .............................. |  | 8 |
| 6.0 |  | Fire detection sensor and alarm initiating device requirements ...................................................................... |  | 9 |
|  | 6.1 | Addressable Breakglass / call point ................................................................................................................. |  | 9 |
|  | 6.2 | Addressable Smoke detector ............................................................................................................................ |  | 9 |
|  | 6.3 | Addressable Heat detector ............................................................................................................................... |  | 9 |
|  | 6.4 | Addressable Interface Module (I/O) ................................................................................................................ |  | 9 |
|  | 6.5 | Short Circuit Isolator ...................................................................................................................................... |  | 9 |
|  | 6.6 | Sprinkler flow switch and sprinkler head ....................................................................................................... |  | 10 |
|  | 6.7 | Alarm bell ...................................................................................................................................................... |  | 10 |
| 7.0 |  | System features .............................................................................................................................................. |  | 11 |
| 8.0 |  | Cable requirements ........................................................................................................................................ |  | 12 |
| 9.0 |  | Optional requirements .................................................................................................................................... |  | 12 |
| 10.0 |  | Technical specifications ................................................................................................................................. |  | 13-22 |
| 11.0 |  | Schedule of prices .......................................................................................................................................... |  | 24 |
| 12.0 |  | Appendix A - Deviation lists ......................................................................................................................... |  | 25 |
| 13.0 |  | Appendix B - System schematic diagram / configuration .............................................................................. |  | 26 |

ANALOGUE ADDRESSABLE FIRE ALARM SYSTEM

| 1.0 |  | SCOPE OF WORKS | Compliance Yes/No |
| --- | --- | --- | --- |
|  | 1.1 | The scope of works call for the supply, install, test, commission, handing over in approved working order and 18 months defect liability maintenance of a complete automatic Analogue Addressable Fire Alarm System and all sensors/ devices in accordance to the specifications and as shown on drawings. |  |
|  |  | The Analogue Addressable Fire Alarm System shall comply to the following rules and regulations. 1.1.1) MS 1745-2 1.1.2) EN 54-2 1.1.3) Requirements of Fire and Rescue Department Malaysia (BOMBA Malaysia) 1.1.4) SIRIM QAS 1.1.5) EMC (Electro Magnetic Compatibility) Test |  |
|  | 1.2 | The contractor shall provide all labour, materials, tools and equipment required to complete the fire alarm system installation. All materials supplied shall be new, free from defects and of best quality of their respective kind. |  |
|  | 1.3 | On completion of the installation, the contractor shall be responsible for obtaining written approval from BOMBA Malaysia and other relevant authorities having jurisdiction, stating that the completed installation is in proper working order. |  |
|  | 1.4 | The cost of all necessary approvals shall be deemed to be included in the contract price. It is also the responsibility of the contractor to enter and expedite all correspondence in connection with the approvals. |  |
|  | 1.5 | Any deviation(s) from the specifications descript hereinafter shall be filled in the deviation list as provided in Appendix A, stating reasons and alternative solution(s), if any. It is understood that any deviations from the specifications may result in the disqualification of tender contract. |  |

| 2.0 |  | GENERAL REQUIREMENTS | Compliance Yes/No |
| --- | --- | --- | --- |
|  | 2.1 | The Fire Alarm System shall be analogue addressable type complete with a Main Fire Alarm Panel (MFAP), addressable fire detection sensors and addressable input and output (I/O) modules, alarm initiating devices and all necessary audio and visual elements. |  |
|  | 2.2 | All locations of all addressable breakglasses, analogue addressable smoke detectors, analogue addressable heat detectors, I/O modules, alarm bells/sounders, sprinkler flow switches and sprinkler heads shown in the drawings are approximate. The contractor shall check the site locations shown on the accompanying drawings and shall adjust accordingly to suit site conditions. Superintending Officer or Consulting Engineer’s approval shall be obtained prior to readjustments or installations. |  |
|  | 2.3 | The contractor shall submit complete detail layout and wiring diagrams, fire alarm system schematic diagram, main fire alarm panel drawings and fire alarm system console/cabinet layout to Superintending Officer or Consulting Engineer for approval at least two (2) weeks prior to commencement of works. |  |
|  | 2.4 | CMS communicator shall be provided for direct linkage, through dedicated telephone line, to nearest fire brigade station’s (Bomba station) CMS for alarm reporting. It shall be able to accept at least volt-free contacts provided by the MFAP. |  |
|  | 2.5 | The system shall be designed to be self supervising to detect and to monitor any wire breakage, unauthorized removal of sensors, to annunciate and to display visual signal at MFAP. It shall be able to initiate fire fighting operations such as annunciation of fire alarm (bell or siren), signal to start pressurization fans, shut down or trip the AHU (air handling unit), trip the lifts, etc. |  |
|  | 2.6 | Self-contained storage batteries complete with charger shall be provided to enable the system to be operational during main power supply and essential power supply failure. During such condition, battery capacity provided shall be able to maintain system operational for at least 72 hours and 1 hours alarm load condition. |  |
|  | 2.7 | A battery calculation data sheet (refer to Appendix B) shall be submitted for approval. |  |
|  | 2.8 | The battery charger shall be capable of charging a fully discharged battery within 24 hours by normal charge method to a fully charged condition. |  |
|  | 2.9 | The system shall operate on incoming 240 Volt AC, 50 Hz main power supply and connected to essential power supply. The incoming main shall then be stepped down to 24 Volt DC for complete usage and operational by the MFAP. |  |
|  | 2.10 | Location of the MFAP shall be in the fire/security control centre as shown in the drawing and the exact position shall be determined at site. |  |
|  | 2.11 | Console/cabinet housing for the MFAP shall allow space to house the mimic panel and standby battery set. |  |
|  | 2.12 | Construction of console/cabinet housing shall have a classification of at least IP 2X. |  |
|  | 2.13 | The MFAP shall consist of System Control Display with 128x64 graphic LCD, Fire Zone Display with 7 units of 16x2 LCD, and Information Display with built-in printer. |  |
|  | 2.14 | System operation shall be by means of alphanumeric keyboard and system operation manual shall be submitted for reference. |  |

| 3.0 |  | SYSTEM REQUIREMENTS. The Fire Alarm System shall consist of the followings :- | Compliance Yes/No |
| --- | --- | --- | --- |
|  | 3.1 | A MFAP and it shall be analogue addressable and come complete with console/cabinet housing to be located at the fire/security control centre. |  |
|  | 3.2 | The MFAP shall consist of System Control Display with 128x64 graphic LCD, Fire Zone Display with 7 units of 16x2 LCD and Information Display with built-in 40 column printer. |  |
|  | 3.3 | A mimic panel and it shall be located at the console/cabinet housing of the MFAP. |  |
|  | 3.4 | Uninterrupted power supply system (batteries) dedicated for providing power to the system during mains power supply failure. |  |
|  | 3.5 | Battery charger mounted within the console/cabinet housing of MFAP. |  |
|  | 3.6 | All necessary audio devices and visual indicators at or within the MFAP. |  |
|  | 3.7 | All necessary fire detection and monitoring sensors. a) Addressable breakglasses/call points b) Addressable smoke detectors c) Addressable heat detectors d) flow switches e) Interface modules (I/O) for indication points. f) Short circuit isolators |  |
|  | 3.8 | All necessary control outputs and alarm initiating devices a) I/O for control output points for lift trip, AHU trip, fan run, etc. b) I/O for alarm bells/sounders. |  |
|  | 3.9 | Volt-free contacts for CMS (Central Monitoring System) interfacing. |  |
|  | 3.10 | Interfacing facilities for Colour Graphic Computer and Building Automation System (BAS). |  |
|  | 3.11 | All the necessary cabling in conduits or trunking for interconnecting the whole system. |  |

| 4.0 |  | FUNCTIONAL REQUIREMENTS. |  | Compliance Yes/No |
| --- | --- | --- | --- | --- |
|  | 4.1 | Alarm condition - This is the transition of the decision element (addressable breakglass/call point, addressable smoke detectors, addressable heat detector, or sprinkler flow switch) from a non-fire state to the fire state and it shall result in the followings:- |  |  |
|  |  | 4.1.1 | Energization of control outputs such as trip the air handling units (AHU), trip the lift, turn on pressurization fan and ventilation fan, etc. as required. |  |
|  |  | 4.1.2 | Energization of alarm initiating devices such as alarm bells or sounders and the sequence of energization shall be two-stage. a) Alarm bells or sounders of the affected floor/level shall be energized permanently. i.e. continuous ringing/sounding. b) Alarm bells or sounders of the adjacent floor/level shall be energized intermittently. i.e. intermittent ringing/sounding (1 second ‘ON’ and 1 second ‘OFF’). |  |
|  |  | 4.1.3 | Energization of an alarm bell or sounder adjacent to or within the MFAP. (usually refer to as MASTER BELL). |  |
|  |  | 4.1.4 | Energization of an internal sounder within the MFAP. (usually refer to as BUZZER). |  |
|  |  | 4.1.5 | A visible indication of the alarm at the MFAP. |  |
|  |  | 4.1.6 | A visible indication of the alarm at the mimic panel. |  |
|  |  | 4.1.7 | In the event of multi-zone operation, a separate and continuous visible indication shall be provided for each alarm zone for items 4.1.5 and 4.1.6. |  |
|  |  | 4.1.8 | Automatic energization of printer for hard copy print-out showing the date, time, type of alarm and location of alarm. |  |
|  | 4.2 | Fault Warning condition - Fault warning shall result in the following :- |  |  |
|  |  | 4.2.1 | An audible warning from a sounder (usually a buzzer) situated at the MFAP and preferably within it. Such warning sounder shall be distinctive and of a different character from any fire alarm sounder. |  |
|  |  | 4.2.2 | The occurrence of a fault in a different zone, or a different fault in the same zone, while the sounder is silenced, shall cause the sounder to sound again. |  |
|  |  | 4.2.3 | A visible indication on the MFAP. |  |
|  |  | 4.2.4 | In the event of multi-zone operation, a separate visible indication shall be provided for each fault warning zone for item 4.2.2. |  |
|  |  | 4.2.5 | The fire alarm condition responses shall not be inhibited by any fault warning unless the fault itself prevents the giving of such responses. |  |
|  |  | 4.2.6 | Fault indications may be suppressed during an alarm condition, but in this case any faults remaining after the alarm condition has been reset shall cause the fault indication to be restored. |  |
|  |  | 4.2.7 | Automatic energization of printer for hard copy print-out showing the date, time, type of fault and location of fault. |  |

| 5.0 |  | SYSTEM DESCRIPTIONS. |  | Compliance Yes/No |
| --- | --- | --- | --- | --- |
|  | 5.1 | System Configuration - A typical system schematic diagram of an Analogue Addressable Fire Alarm System shall be as shown in Appendix C. It shall consist of two (2) basic portions as detailed in items 5.1.1, and 5.1.2. |  |  |
|  |  | 5.1.1 | A Main Fire Alarm Panel (MFAP). |  |
|  |  | 5.1.2 | All fire detection sensors, monitoring sensors, control outputs, and alarm initiating devices. |  |
|  | 5.2 | Main Fire Alarm Panel (MFAP) - This shall be the central controller. All information processing, monitoring of input points, and controlling of output points shall be done here. The processed data shall then be converted to understandable audio and visual information. It shall consist of the following essential components :- 1) System Control Display - Central controller 2) Fire Zone Display - LCD and LED for alarm, fault and disable indications 3) Information Display with built-in 40 column printer 4) Mimic panel, 5) Battery charger, and 6) 24 V DC battery set |  |  |
|  |  | 5.2.1 | System Control Display (Central controller) - This shall form the ‘brain’ of the complete system. All information shall be processed and displayed into meaningful messages at LED and LCD panels, mimic panel, and appropriate print-out at printer. It shall consist of the following elements. - LED indicators for - Power ON - System FAULT - AC Power FAULT - Battery FAULT - Earth FAULT - FIRE, FAULT and DISABLE - AUTO and MANUAL Evacuate - Sounder Disable - General Test - Miscellaneous Status - Delay to Output Override b) TEST LAMP/LCD, TEST BUZZER, and SILENCE BUZZER keys c) LCD - 128x64 graphic display d) "0 - 9" alphanumeric and scroll keys e) CONTROL ACCESS keyswitch |  |
|  |  | 5.2.2 | Fire Zone Display. It shall consist of the following elements. a) 7 units of 16x2 LCD b) LEDs for FIRE, FAULT, DISABLE and QUEUE |  |
|  |  | 5.2.3 | Information Display - It shall contain - System operation instructions both in English and Bahasa - Built-in 40 column printer - This shall be the event logger for permanent recording of any event happening. Every event print-out shall show the date and time, zone and/or location of the event, type of event, and status of event. |  |
|  |  |  |  | Compliance Yes/No |
|  |  | 5.2.4 | Mimic panel - This shall consist of all floor plans and section of the building, printing on a perspex plastic sheet. It shall be multi-colour. There shall be LEDs on the mimic floor plans to indicate location of each alarm zone. As a general rule, colour of the areas shall be as follows :- a) All escape staircases - yellow b) All M & E rooms relating to fires (eg. Fire pump room, Fan room, etc) - red c) All M & E rooms not relating to fires (eg. AHU room, Computer room, etc) - orange d) All lifts and lift lobbies - brown e) All other enclosed areas surrounded by walls - blue f) All lines, wordings and symbols - black g) Background - white |  |
|  |  | 5.2.5 | Battery charger and power supply unit - This shall form the source of power supply for the complete fireman intercom system. The battery charger shall be able to provide boost charge. Input voltage to the charger shall be 240 volts AC, 50 Hz. Output voltage from the charger shall be regulated to 27.5-28.5 volts DC depending on type of battery used. The power supply unit shall convert the incoming 27.5-28.5 volts DC to other voltages required by other components and modules within the system. The charger shall be capable of charging a fully discharged battery within 24 hours by normal charge method to a fully charged condition. It shall be protected against short circuit with automatic over-current shutdown. The charger shall be of linear, constant voltage charging type to prevent unnecessary damages or shortening the lifespan of battery. When the battery is fully charged, the charger shall automatically switch to float charging. |  |
|  |  | 5.2.6 | 24 volts DC battery set - This shall form as backup/standby power supply in case of 240 V main AC failure. It shall be sealed lead acid type of sufficient capacity to maintain the system operational for at least 72 hours in case of 240 V mains AC failure. In addition, it shall be capable of supplying full emergency evacuation alarm load of at least 1 hour. The battery set shall be mounted in the lower compartment of the console/cabinet housing and the charging equipment shall be installed above it and readily accessible. |  |
|  | 5.3 | Fire Detection Sensors, Monitoring Sensors, Control Outputs and Alarm Initiating Devices - These shall be the reporting and energizing elements to the MFAP. |  |  |
|  |  | 5.3.1 | Fire detection sensors - These shall form the whole part of alarm zones. Depending on design requirements, they shall consist of addressable smoke detectors, addressable heat detectors, flow switches, and addressable breakglasses/call points. |  |
|  |  | 5.3.2 | Monitoring sensors - These shall form the whole part of status indications. Depending on design requirements, they shall consist of fire pump indications, fire tank indications, CO2/FM 200 indications, gen-set indications, butterfly/subsidiary valve indications, AHU run indications, fan trip indications, and etc. |  |
|  |  | 5.3.3 | Control outputs - These shall form the whole part of the events/equipments energization sequence. Depending on design requirements, they shall consist of AHU trip, lift trip, fan run, fire damper open, magnetic door close, and etc. |  |
|  |  | 5.3.4 | Alarm initiating devices - These shall form the whole part of alert/evacuation energization sequence. Depending on design requirements, they shall consist of alarm bells, sirens, flashing lights, and other forms of sounders and visual elements. |  |
| 6.0 |  | FIRE DETECTION SENSOR AND ALARM INITIATING DEVICE REQUIREMENTS |  | Compliance Yes/No |
|  | 6.1 | Addressable breakglass/call point - It shall be provided with EN 54-11, MS 1745-11 and BOMBA approvals. - It shall be bright red in colour, flushed/surface mounting type. - It shall be constructed from shatterproof and corrosion resistance self extinguishing plastic case suitable for 20 mm conduit entry and a breakable glass with appropriate label/symbol. - It shall be suitable for operation on 24 V DC. - It shall be fixed at a height to be determined on site and generally at 1500mm above floor level. - For outdoor installation, it shall be of weatherproof type to IP 54. - Address setting shall be DIP switch type or soft addressing type. |  |  |
|  | 6.2 | Addressable smoke detector - It shall be provided with EN 54-7 and BOMBA approvals. - It shall be photoelectric/optical type. - Separate mounting base shall be required for the detector. - Colour of the detector and base shall be off-white and constructed from corrosion resistant self extinguishing plastic. - It shall be suitable for operation on 24 V DC. - It shall be suitable for protecting an area of up to 100 sq. m. at a height of up to 12 m. - 2 LED indicators shall be provided in each detector which illuminates on triggering. - Address setting shall be DIP switch type or soft addressing type. - It shall be able to provide analogue signal. |  |  |
|  | 6.3 | Addressable heat detector - It shall be provided with EN 54-5 and BOMBA approvals. - It shall be of “rate of rise and fix temperature” combined type. - Separate mounting base shall be required for the detector. - Colour of the detector and base shall be off-white and constructed from corrosion resistant self extinguishing plastic. - It shall be suitable for operation on 24 V DC. - It shall be suitable for protecting an area of up to 50 sq. m. at a height of up to 13 m. - 2 LED indicators shall be provided in each detector which illuminates on triggering. - Address setting shall be DIP switch type or soft addressing type. - It shall be able to provide analogue signal. |  |  |
|  | 6.4 | Addressable interface module (I/O) - It shall be provided with EN 54-18 and BOMBA approvals. - It shall be suitable for operation on 24 V DC. - It shall be housed inside a weatherproof IP 54 plastic casing. - It shall be capable of accepting up to 4 input points, or 1 input & 1 output. - Address setting shall be DIP switch type or soft addressing type. |  |  |
|  | 6.5 | Addressable Short circuit isolator base - It shall be installed between every 20 detectors. - It shall be suitable for operation on 24 V DC. - In case of short circuit, only the affected segment shall be disabled. - It shall also act as base for detectors. |  |  |

|  |  |  |  | Compliance Yes/No |
| --- | --- | --- | --- | --- |
|  | 6.6 | Sprinkler flow switch and sprinkler head - It shall be provided with UL and BOMBA approvals. - The sprinkler flow switch shall be paddle type, fitted with a 5 second solid state delay relay to prevent false alarm caused by water surge in the system. - The flow switch shall be installed at location such that it is at least 5 times diameter of pipe away from the butterfly isolation valve. - The sprinkler head shall be glass bulb type and in general, the temperature rating shall be 68 degree C (155 degree F). - Unless otherwise approved, the deflector shall be of universal type to enable the sprinkler to be suitable for operation in either upright or pendant position. - The sprinkler head shall produce a spherical discharge with a proportion of water being thrown upwards. It shall be chrome/bronze plated finishing and complete with colour matched escutcheon. |  |  |
|  | 6.7 | Alarm bell - It shall be provided with EN 54-3, MS 1745-3 and BOMBA approvals. - It shall be motorized type with low current consumption. - Colour of the bell shall be red, 150 mm in diameter and surface mounted type. - It shall be constructed from pressed steel with stove enamelled finishing. - The decibel rating of the bell shall be at least 90db with respect to the surrounding sound level. - It shall be installed 2.5 m above floor level. - It shall be suitable for operation on 24 V DC. - For outdoor installation, it shall be of weatherproof type to IP 54. |  |  |
| 7.0 |  | SYSTEM FEATURES |  | Compliance Yes/No |
|  | 7.1 | The MFAP shall be analogue addressable type. |  |  |
|  | 7.2 | A standard MFAP shall have a capacity to handle up to 16 loops and 600 fire zones. |  |  |
|  | 7.3 | A 128x64 LCD graphic arranged in "ATM" format shall be provided. |  |  |
|  | 7.4 | System operation shall be through alphanumeric keyboard. |  |  |
|  | 7.5 | Real time event memory of up to 1000 alarm log and 600 general fault/disable log shall be provided. |  |  |
|  | 7.6 | System modules shall be interchangeable from one to another. |  |  |
|  | 7.7 | The MFAP shall be able to interface to 40 column printer for event printing. |  |  |
|  | 7.8 | The MFAP shall be able to interface to BAS (Building Automation System) through RS 232 serial communication or volt-free contacts. |  |  |
|  | 7.9 | The MFAP shall be able to interface to CMS (Central Monitoring System) for direct linkage to Bomba (fire authority) through volt-free contacts. |  |  |
|  | 7.10 | The MFAP shall be able to interface to colour graphic computer for dynamic graphic display of alarm occurrence. A genuine graphic software (WINFSS) with certificate shall be provided. |  |  |
|  | 7.11 | A real time clock shall be incorporated. |  |  |
|  | 7.12 7.13 7.14 | Password/access level shall be incorporated for security purpose. Fire Zone Display shall consists of 7 units of 16x2 LCD and separate LEDs for displaying Fire , Fault and Disable conditions. System/operation instruction on the 128x64 LCD graphic display shall be able to display text in Bahasa Malaysia. |  |  |
|  | 7.15 | Capability for system interlinking using fibre optic cable shall be provided. All necessary fibre optic converter, modem, patch panel, etc shall be provided for complete system functioning. |  |  |
| 8.0 |  | CABLE REQUIREMENTS |  | Compliance Yes/No |
|  | 8.1 | A typical system wiring diagram shall be as shown in Appendix B. |  |  |
|  | 8.2 | Looping cables from MFAP to detectors/devices and back to the MFAP (Ring circuit)shall be as follows :- |  |  |
|  |  | 8.2.1 | For Indoor Installation, - 2 x 1.5 mm-sq PVC cables and non-twisted for up to 1.2km. OR - 2 x 1.5 mm-sq PVC cable and twisted for up to 2km. |  |
|  |  | 8.2.2 | For Outdoor Installation, - 2 x 1.5 mm-sq armoured cables and non-twisted for up to 1.2km. OR - 2 x 1.5 mm-sq armoured cable and twisted for up to 2km. |  |
|  | 8.3 | Looping cable size chosen for bells and controls power supply shall be such that during alarm bells ringing and control outputs energisation, the voltage reaching the furthest bell and control point shall not be less than 22 volts DC. |  |  |
| 9.0 |  | OPTIONAL REQUIREMENTS |  |  |
|  | 9.1 9.2 | Colour Graphic Computer - The software provided shall be able to operate, identify and display alarm and fault conditions on the dynamic floor plans. It shall consist of a CPU, RAM., DVD Drive, Hard Disk, Serial and Parallel Cards, Keyboard, Power Supply, Colour Monitor, UPS for 20 minutes and other necessary components to form a complete system. Lightning Surge Arrestor - Appropriate lightning surge arrestor shall be provided for 240 VAC line, 24 VDC power line and looping signal data line. |  |  |

| 10.0 | TECHNICAL SPECIFICATIONS |  |  |  |
| --- | --- | --- | --- | --- |
|  | 10.1 | 10.1.1 10.1.2 10.1.3 10.1.4 10.1.5 10.1.6 10.1.7 10.1.8 10.1.9 10.1.10 10.1.11 10.1.12 10.1.13 | Main Fire Alarm Panel Manufacturer / Country --------- Brand ------------------------------ Model -------------------------------- Part Number ------------------------- Operating Voltage ---------------- Operating Temperature --------- Operating Humidity -------------- Panel Construction ---------------- Finishing ----------------------- Colour ------------------------- Dimension ----------------------- Weight --------------------------- Approved Standard ------ ----- | Micro-CTL Automation Sdn Bhd / Malaysia ---- Mictron ---- 9900 ---- AXP-M9900 Input 220-240VAC/50Hz, Output 24VDC ---- 0 – 45 Degree C 95% RH (non – condensation) ---- Mild Steel ---- Epoxy powder coated paint, oven baked ---- red --- 720mm (W)x430mm(H)x150mm(D) 18.6kg (exclude battery) EN 54-2, MS 1745-2 |
|  | 10.2 | 11.3.1 11.3.2 11.3.3 11.3.4 11.3.5 11.3.6 11.3.7 11.3.8 | Power Supply and Charger Manufacturer / Country --------- Brand ------------------------------ Type -------------------------------- Input Voltage --------------------- Output Voltage ------------------- Type of power Switches --------- Operating Temperature ---------- Operating Humidity -------------- | ---- Micro-CTL Automation Sdn Bhd / Malaysia ---- Mictron ---- Constant Voltage and Current ---- 220 - 240VAC, 50Hz, Single phase ---- 27.5VDC, 5A maximum ---- AC on, CPU on, RPPU/LC on, BELL on ---- 0 – 45 degree C ---- 95% RH (non-condensation) |

|  | 10.3 | 10.3.1 10.3.2 10.3.3 10.3.4 10.3.5 10.3.6 10.3.7 10.3.8 |  | Colour Mimic Panel Manufacturer / Country --------- Brand ------------------------------ Model ------------------------------ Type -------------------------------- Material ---------------------------- Operating Voltage ---------------- Operating Temperature ---------- Operating Humidity -------------- |  | ---- Micro-CTL Automation Sdn Bhd/ Malaysia ---- Mictron M9900 – mimic ---- Colour printing or silkscreen ---- Perspex sheet 24VDC ---- 0 – 45 degree C ---- 95% RH (non-condensation) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 10.4 | 10.4.1 10.4.2 10.4.3 10.4.4 10.4.5 10.4.6 10.4.7 10.4.8 10.4.9 10.4.10 10.4.11 10.4.12 10.4.13 10.4.14 10.4.15 |  | Addressable Breakglass /Call Point Manufacturer / Country --------- Brand ------------------------------- Model ------------------------------ Part Number ------------------------ Quiescent Current ------------------ Alarm Current ----------------------- Operating Voltage ------------------ Type -------------------------------- Temperature Range --------------- Operating Humidity --------------- Weight ------------------------------- Material ------------------------------ Dimension (mm) -------------------- Colour -------------------------------- Approved Standard ----------------- |  | Micro-CTL Automation Sdn Bhd / Malaysia Mictron Series AX AX-9BG 800 uA 1.6 mA 18 - 28 VDC Non-resettable -20 to 70 degree C 95% RH (non-condensation) 140 g ABS 88mm x 88mm x 59mm red EN 54-11, MS 174-11 |  |  |  |
|  | 10.5 | 10.5.1 10.5.2 10.5.3 10.5.4 10.5.5 10.5.6 10.5.7 10.5.8 10.5.9 10.5.10 10.5.11 10.5.12 10.5.13 10.5.14 10.5.15 10.5.16 |  | Addressable Smoke Detector Manufacturer / Country --------- Brand ------------------------------- Model ------------------------------ Part Number ------------------------ Quiescent Current ------------------ Alarm Current ----------------------- Operating Voltage ------------------ Type -------------------------------- Temperature Range --------------- Operating Humidity --------------- Weight ------------------------------- Material ------------------------------ Dimension (mm) -------------------- Colour -------------------------------- Approved Standard ----------------- Analogue capability ---------------- |  | Micro-CTL Automation Sdn Bhd / Malaysia Mictron Series AX AX-9SL 500 uA 7 mA 17 - 28 VDC Photoelectric -10 to 50 degree C 95% RH (non-condensation) 150 g with base ABS 100mm (diameter) x 46mm (depth) with base White EN 54-7 Yes |  |  |  |
|  | 10.6 | 10.6.1 10.6.2 10.6.3 10.6.4 10.6.5 10.6.6 10.6.7 10.6.8 10.6.9 10.6.10 10.6.11 10.6.12 10.6.13 10.6.14 10.6.15 10.6.16 |  | Addressable Heat Detector Manufacturer / Country --------- Brand ------------------------------- Model ------------------------------ Part Number ------------------------ Quiescent Current ------------------ Alarm Current ----------------------- Operating Voltage ------------------ Type -------------------------------- Temperature Range --------------- Operating Humidity --------------- Weight ------------------------------- Material ------------------------------ Dimension (mm) -------------------- Colour -------------------------------- Approved Standard ----------------- Analogue capability ---------------- | Micro-CTL Automation Sdn Bhd / Malaysia Mictron Series AX AX-9HL 500 uA 7 mA 17 - 28 VDC ROR & Fixed Temperature -10 to 50 degree C 95% RH (non-condensation) 150 g with base ABS 100mm (diameter) x 46mm (depth) with base White EN 54-5 Yes |  |  |  |  |
|  | 10.7 | 10.7.1 10.7.2 10.7.3 10.7.4 10.7.5 10.7.6 10.7.7 10.7.8 10.7.9 10.7.10 10.7.11 10.7.12 10.7.13 10.7.14 10.7.15 |  | Input Interface Module Manufacturer / Country --------- Brand ------------------------------- Model ------------------------------ Part Number ------------------------ Quiescent Current ------------------ Alarm Current ----------------------- Operating Voltage ------------------ Type -------------------------------- Temperature Range --------------- Operating Humidity --------------- Weight ------------------------------- Material ------------------------------ Dimension (mm) -------------------- Colour -------------------------------- Approved Standard ----------------- | Micro-CTL Automation Sdn Bhd / Malaysia Mictron Series AX AXM-1ZV-B 1.4 mA N/A 20 - 28 VDC 4-inputs 0 to 50 degree C 95% RH (non-condensation) 180 g with enclosure ABS 110mm x 110mm x 55mm Light grey EN 54-18 |  |  |  |  |
|  | 10.8 | 10.8.1 10.8.2 10.8.3 10.8.4 10.8.5 10.8.6 10.8.7 10.8.8 10.8.9 10.8.10 10.8.11 10.8.12 10.8.13 10.8.14 10.8.15 |  | Output Interface Module Manufacturer / Country --------- Brand ------------------------------- Model ------------------------------ Part Number ------------------------ Quiescent Current ------------------ Alarm Current ----------------------- Operating Voltage ------------------ Type -------------------------------- Temperature Range --------------- Operating Humidity --------------- Weight ------------------------------- Material ------------------------------ Dimension (mm) -------------------- Colour -------------------------------- Approved Standard ----------------- | Micro-CTL Automation Sdn Bhd / Malaysia Mictron Series AX AXM-1ZV-A 1.4 mA 3-7 mA (Output on) 20 - 28 VDC 1-output /sounder and 1-input 0 to 50 degree C 95% RH (non-condensation) 180 g with enclosure ABS 110mm x 110mm x 55mm Red EN 54-18 |  |  |  |  |
|  | 10.9 | 10.9.1 10.9.2 10.9.3 10.9.4 10.9.5 10.9.6 10.9.7 10.9.8 10.9.9 10.9.10 10.9.11 10.9.12 10.9.13 10.9.14 10.9.15 |  | Short Circuit Isolator Manufacturer / Country --------- Brand ------------------------------- Model ------------------------------ Part Number ------------------------ Quiescent Current ------------------ Alarm Current ----------------------- Operating Voltage ------------------ Type -------------------------------- Temperature Range --------------- Operating Humidity --------------- Weight ------------------------------- Material ------------------------------ Dimension (mm) -------------------- Colour -------------------------------- Approved Standard ----------------- | Micro-CTL Automation Sdn Bhd / Malaysia Mictron Series AX AX-9SCI 30 uA 2 mA 17 - 28 VDC Resettable -20 to 70 degree C 95% RH (non-condensation) 25 g with enclosure ABS 100mm (diameter)x 20mm (depth) White N/A |  |  |  |  |
|  | 10.10 | 10.10.1 10.10.2 10.10.3 10.10.4 10.10.5 10.10.6 10.10.7 10.10.8 10.10.9 10.10.10 10.10.11 10.10.12 10.10.13 |  | Sprinkler Flow Switch Manufacturer / Country --------- Brand ------------------------------- Model ------------------------------ Part Number ------------------------ Operating Voltage ------------------ Type -------------------------------- Temperature Range --------------- Operating Humidity --------------- Weight ------------------------------- Material ------------------------------ Dimension (mm) -------------------- Colour -------------------------------- Approved Standard ----------------- |  |  |  |  |  |
|  | 10.11 | 10.11.1 10.11.2 10.11.3 10.11.4 10.11.5 10.11.6 10.11.7 10.11.8 10.11.9 10.11.10 10.11.11 10.11.12 10.11.13 |  | Sprinkler Head Manufacturer / Country --------- Brand ------------------------------- Model ------------------------------ Part Number ------------------------ Operating Voltage ------------------ Type -------------------------------- Temperature Range --------------- Operating Humidity --------------- Weight ------------------------------- Material ------------------------------ Dimension (mm) -------------------- Colour -------------------------------- Approved Standard ----------------- |  |  |  |  |  |
|  | 10.12 | 10.12.1 10.12.2 10.12.3 10.12.4 10.12.5 10.12.6 10.12.7 10.12.8 10.12.9 10.12.10 10.12.11 10.12.12 10.12.13 10.12.14 10.12.15 |  | 6" Alarm Bell Manufacturer / Country --------- Brand ------------------------------- Model ------------------------------ Part Number ------------------------ Alarm Current ------------------ Sound Output ---------------------- Operating Voltage ------------------ Type -------------------------------- Temperature Range --------------- Operating Humidity --------------- Weight ------------------------------- Material ------------------------------ Dimension (mm) -------------------- Colour -------------------------------- Approved Standard ----------------- | Micro-CTL Automation Sdn Bhd / Malaysia Mictron Series C C-9BL 30 mA 95 dBA 20 - 28 VDC DC Motor -20 to 60 degree C 95% RH (non-condensation) 764 g High Quality Steel 150mm (diameter)x 56mm (depth) Red EN 54-3, MS 1745-3 |  |  |  |  |
|  | 10.13 | 10.13.1 10.13.2 10.13.3 10.13.4 10.13.5 10.13.6 10.13.7 10.13.8 10.13.9 10.13.10 10.13.11 10.13.12 |  | Lightning Surge Arrestor (240 VAC) Manufacturer / Country --------- Brand ------------------------------- Model ------------------------------ Part Number ------------------------ Maximum AC Voltage ----------- Maximum Discharge Current ---- Response Time -------------------- Type -------------------------------- TOV Voltage ----------------------- Temperature Range --------------- Material ------------------------------ Approved Standard ----------------- | Dehn & Sohne / Germany Dehn DG T 275 & DGP CT 255 900 650 & 900 133 275 V & 255 V 20 kA (8/20uS) & 40 kA (8/20 uS) <= 25 nS & <= 100 uS Type 2 / Class 2 335 V / 5 Sec & 1200 V / 200 mS -40 deg C to +80 deg C Red Thermoplastic IEC 61643-1 |  |  |  |  |
|  | 10.14 | 10.14.1 10.14.2 10.14.3 10.14.4 10.14.5 10.14.6 10.14.7 10.14.8 10.14.9 10.14.10 10.14.11 |  | Lightning Surge Arrestor (24 VDC Power Line) Manufacturer / Country --------- Brand ------------------------------- Model ------------------------------ Part Number ------------------------ Maximum DC Voltage ----------- Maximum Discharge Current ---- Response Time -------------------- Type -------------------------------- Temperature Range --------------- Material ------------------------------ Approved Standard ----------------- | Dehn & Sohne / Germany Dehn DR M 2P 30 953 201 30 V 2 kA (8/20uS) <= 100 nS Type 3 / Class 3 -40 deg C to +80 deg C Red Thermoplastic IEC 61643-1 |  |  |  |  |
|  | 10.15 | 10.15.1 10.15.2 10.15.3 10.15.4 10.15.5 10.15.6 10.15.7 10.15.8 10.15.9 10.15.10 10.15.11 |  | Lightning Surge Arrestor (24 VDC Signal/Data Line) Manufacturer / Country --------- Brand ------------------------------- Model ------------------------------ Part Number ------------------------ Maximum DC Voltage ----------- Maximum Discharge Current ---- Series Impedance per Line ------- Type -------------------------------- Temperature Range --------------- Material ------------------------------ Approved Standard ----------------- | Dehn & Sohne / Germany Dehn DCO RK ME 24 919 921 33 V 10 kA (8/20uS) 1.8 ohms Type 2 -40 deg C to +80 deg C Polyamide PA 6.6 IEC 61643-21 |  |  |  |  |
|  | 10.16 | 10.16.1 10.16.2 10.16.3 10.16.4 10.16.5 10.16.6 |  | # OPTIONAL ITEMS Colour Graphic Computer Manufacturer --------------------- Brand ------------------------------- Model ------------------------------ Type of Processor ---------------- Colour Monitor size -------------- Other features ---------------------- |  |  |  |  |  |
| 11.0 |  | ##### SCHEDULE OF PRICES |  |  |  |  |  |  |  |
|  | 11.1 |  | MAIN FIRE ALARM PANEL (MFAP) |  |  |  | ###### QTY | UNIT PRICE (RM.) | TOTAL (RM.) |
|  |  | 11.1.1 11.1.2 11.1.3 | CPU central controller, loop controller , power supply and charger, built-in printer, and software. Mimic panel complete with multi-colour plans, LEDs and mimic LED driver cards. Sealed lead acid battery AH 24 V DC |  |  |  |  |  |  |
|  | 11.2 |  | Console housing for items 11.1.1 to 11.1.3 (optional) |  |  |  | C |  |  |
|  | 11.3 |  | Addressable breakglasses/call points |  |  |  |  |  |  |
|  | 11.4 |  | Addressable smoke detectors |  |  |  |  |  |  |
|  | 11.6 |  | Addressable heat detectors |  |  |  |  |  |  |
|  | 11.7 |  | Addressable interface modules (I/O) |  |  |  |  |  |  |
|  | 11.8 |  | Short circuit isolators |  |  |  |  |  |  |
|  | 11.9 |  | Sprinkler flow switches |  |  |  |  |  |  |
|  | 11.10 |  | Sprinkler heads complete with escutcheons |  |  |  |  |  |  |
|  | 11.11 |  | Sprinkler heads without escutcheons |  |  |  |  |  |  |
|  | 11.12 |  | Lightning surge arrestors |  |  |  |  |  |  |
|  | 11.13 |  | Alarm bells |  |  |  |  |  |  |
|  | 11.14 |  | Lump sum wiring, conduits and/or trunkings |  |  |  |  |  |  |
|  | 11.15 |  | Lump sum installation work,inclusive of testing and commissioning. |  |  |  |  |  |  |
|  | 11.16 |  | Optional item. a) Colour graphic computer complete with all necessary hardware and software. |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | TOTAL |  |

| 12.0 | APPENDIX A - DEVIATION LISTS |
| --- | --- |
| Items deviated | Reason and alternative solution(s) |

13.0   APPENDIX B - SYSTEM SCHEMATIC DIAGRAM / CONFIGURATION.

Last updated: 1/1/2015